## 1. Background & Instructions
Industrial Heat Pump Procurement Toolkit
Background
Industrial heat pumps (IHPs) are a critical technology for enabling the electrification of industrial process heating, as well as district and local heating. Manufacturing facilities that are considering IHPs must have data on their processes to determine which types of IHPs are a good fit, and to decide on competitive bids. Suppliers of IHPs need to understand the technical, environmental, economic, and regulatory requirements of individual facilities to determine whether one of their products may be suited to specific applications. In many cases, a list of critical data points from interested facilities can reduce the iterative costs of site visits or multiple conversations to select equipment.
Broadly, IHPs work best for applications where:
- Process heating loads require temperatures of 250°F/121°C or less, such as water heating for cleaning, pasteurization, drying, etc. (hot water heat pumps).
- Steam is used for facility-wide process heating at temperatures and pressures up to 420°F/216°C and 300 psig (steam-generating heat pumps).
- Process heating operations run for more than 4,000 hours per year.
- There are simultaneous, co-located heating and cooling needs.
- There are waste heat recovery opportunities from un-economized boilers, refrigeration condenser coils, compressed air heat exhaust, dryer exhaust or other process heat load discharge that is 80°F/27°C or greater and, in aggregate, greater than 1 million BTUs/hour or comparable to the size of the heating load.
This list is not exhaustive. There may be other applications where IHPs could work well (e.g., with natural/ambient heat sources), and suppliers are actively developing heat pumps with higher temperatures and capacities.
Instructions
The questions in this toolkit are essential for potential IHP buyers to answer before pursuing vendors and/or quotes for IHP technology. The answers to these questions should be further discussed with potential vendors, but knowing the answers in advance will be critical to efficiently evaluating technology fit.
The toolkit should be completed for a particular process where IHPs could apply. An energy assessment of the entire facility or plant could be used to determine the specific processes and locations that are best suited for IHPs. Please complete an individual toolkit for each process or location under consideration.
Follow the steps below:
Step 1: | Provide your contact information in 2. Your Contact Info.
Step 2: | Answer the questions in 3. Questionnaire.
Please provide as much detail as possible and answer as many questions as you can. The questions of highest priority to IHP suppliers are bolded.
To see what a completed questionnaire could look like, view 5. Questionnaire Example.
Step 3: | If possible, please insert a process diagram in 4. Process Diagram.
Step 4: | After completing steps 1-3, send this Excel file to the list of IHP suppliers provided on 6. IHP Suppliers List via email.
Resources
For additional information on IHPs, their savings potential, and their fit for certain applications, please consult:
Resources on ACEEE’s IHP Landing Page
RTC’s Heat Pump Decision Support Tools
For facilities without the ability to determine the answers to these questions, several resources can help, including energy audits (through utilities or state programs) and energy assessments from:
Technical Assistance Partnerships
Industrial Assessment Centers
Third party engineering firms
Please reach out to the contacts below for additional information.
ACEEE:
Andrew Hoffmeister - ahoffmeister@aceee.org
Hellen Chen - hchen@aceee.org
NEMA:
Steve Griffith - steve.griffith@nema.org
RTC:
Ruth Checknoff - ruth@dgardiner.com |  | Last updated: | 2024-10-17

## 2. Your Contact Info
Please enter your contact information:
Name(s):
Company:
Title:
Email:
Phone Number:

## 3. Questionnaire
Topic |  | Question | Answer | Units (choose from dropdown) | Comments (optional)
Note: Bolded questions are highest priority. Please answer as many questions as you can and use the comments section to provide further details.
| General Information | Describe the process under consideration (e.g., drying, distilling, pasteurizing, etc.). |  | n/a
|  | Where is the facility located? Be as specific as you can (e.g., address, state, region, etc.). |  | n/a
|  | What are your schedule requirements? Are you looking to install a heat pump by a specific date? |  | n/a
Technical – System requirements
| Heat Source | What are the potential heat sources (i.e., heat pump inlets, waste heat sources) of the process? |  | n/a
What is the minimum supply temperature?
What is the maximum supply temperature?
How much waste heat is available?
| Heat Sink | What are the potential heat sinks (i.e., heat pump outlet(s), heat load) of the process? |  | n/a
What is the temperature required for the heat sink (i.e., what temperature must the heat pump lift to)?
How much heat is required?
For steam applications, how much, if any, superheat is required?
Describe the operating schedule of the heat load on a daily or weekly basis (e.g., 24/7, 24/5, day shift only, etc.).
|  | How many hours per year is the heat needed? |  | hrs/yr
| Distance | What is the distance between the heat sink and heat source?
| Working Fluids | What are the working fluid(s) for the heat sink and source? |  | n/a
| Current Heating System | What is the heating capacity of the facility’s current heating system?
What is the hot water temperature setpoint of the facility’s current heating system?
What is the steam pressure setpoint of the facility’s current heating system?
|  | Are there other setpoints of the facility’s current heating system? Please specify in comments. |  | specify
What is the baseload heat demand of the facility’s current heating system?
What is the peak heat demand of the facility’s current heating system?
| Capacity Expansion | Do you want to expand your process heating capacity? If so, please explain in the comments.
Do you want to expand your process cooling capacity? If so, please explain in the comments.
| Partial-Load Operation | How is partial-load operation planned (e.g., fixed volume flow, variable temperatures, etc.)? |  | n/a
Energy-related requirements and costs
| Fuel Consumption and Costs | How much fuel did the process consume over the past 12 months?
|  | What fuel was used for the process? |  | n/a
What was your average fuel price over the past 12 months?
|  | Were these fuel prices fixed or variable? |  | n/a
|  | Do you expect your fuel price to change in the next 12 months? If so, please explain in the comments. |  | n/a
|  | How much electricity did the process consume over the past 12 months? |  | kWh
|  | What was your average electricity price over the past 12 months? |  | $/kWh
|  | What was your average peak demand electricity price over the past 12 months? |  | $/kW
|  | Were these electricity prices fixed or variable? |  | n/a
|  | Do you expect your electricity price to change in the next 12 months? If so, please explain in the comments. |  | n/a
| Electrical Service | What is the total capacity (MW) of available electrical service on site? |  | MW
|  | How much electrical margin reserve do you have available on site? |  | MW
| Onsite Renewables | Are any renewable energy technologies (e.g., thermal energy storage tanks, electric boilers) already deployed on site? If so, please explain in the comments. |  | n/a
|  | Are you interested in integrating IHPs with other renewable energy technologies? |  | n/a
Environmental – Site considerations
| Site Temperatures | What is your site's average ambient air temperature (if seeking air source heat pump)?
What is your site's minimum ambient air temperature (if seeking air source heat pump)?
What is your site's maximum ambient air temperature (if seeking air source heat pump)?
| Noise Requirements | Do you have noise requirements to comply with? (E.g., according to OSHA, a worker should not be exposed to more than 85 dB of noise over an 8-hour period.) |  | n/a
| Floor Space | How much available floor space does your site have to accommodate a heat pump?
| Refrigerants | Other than HVAC systems, what refrigerants do you have on site? |  | n/a
|  | Do you have one or more preferred refrigerant? |  | n/a
|  | Do you have any refrigerant restrictions? If so, please select from the dropdown and explain in the comments. |  | n/a
| Retrofits | Are you retrofitting an existing system or adding a new one? |  | n/a
| Redundancy | Do you have redundancy requirements? If so, what are they? |  | n/a
Economic – Institutional and financial considerations
| Goals | What is your main goal in installing a heat pump (e.g., efficiency gains, cost savings, decarbonization targets)? |  | n/a
| Incentives | Have you accessed any utility, state, or federal incentives to help fund this heat pump project? If so, please select one or more funding types from the dropdown. |  | n/a
|  | Are you interested in any utility, state, or federal incentives to help fund this heat pump project? If so, please select one or more funding types from the dropdown. |  | n/a
|  | Do you need to comply with any related requirements? Please explain in the comments. |  | n/a
| OpEx Requirements | Do you have internal operating expense (OpEx) or payback requirements? |  | n/a
| Internal Carbon Price | If your company has set an internal carbon price, what is it? |  | $/MMT CO2
Regulatory – Certifications and compliance
| UL Certification | Do you need UL (Underwriters Laboratories) certification on the cabinet and/or the whole heat pump? |  | n/a
| Good Manufacturing Practices | Do you require GMP paperwork, or post-installation inspections? |  | n/a
| Insurance | Do you need to comply with any requirements or standards from your insurance company? |  | n/a
| Local Codes | Do you need to comply with any local codes that might impact this project? |  | n/a

## 4. Process Diagram
Please provide a process diagram and describe how your process operates.
Please insert an image of this diagram below, if available:
Please describe the diagram in words:

## 5. Questionnaire Example
Topic |  | Question | Answer | Units (choose from dropdown) | Comments (optional)
Note: Bolded questions are highest priority. Please answer as many questions as you can and use the comments section to provide further details.
| General Information | Describe the process under consideration (e.g., drying, distilling, pasteurizing, etc.). | Wash water | n/a
|  | Where is the facility located? Be as specific as you can (e.g., address, state, region, etc.). | 1234 Street, CA, 84106 | n/a
|  | What are your schedule requirements? Are you looking to install a heat pump by a specific date? | Yes, install by Q4 2025 | n/a
Technical – System requirements
| Heat Source | What are the potential heat sources (i.e., heat pump inlets, waste heat sources) of the process? | Refrigeration condensing | n/a
|  | What is the minimum supply temperature? | 60 | °F
|  | What is the maximum supply temperature? | 80 | °F
|  | How much waste heat is available? | 2.5 | MW
| Heat Sink | What are the potential heat sinks (i.e., heat pump outlet(s), heat load) of the process? | Heat wash water | n/a
|  | What is the temperature required for the heat sink (i.e., what temperature must the heat pump lift to)? | 145 | °F
|  | How much heat is required? | 1.9 | MW
For steam applications, how much, if any, superheat is required?
|  | Describe the operating schedule of the heat load on a daily or weekly basis (e.g., 24/7, 24/5, day shift only, etc.). | See comments |  | Clean up at night for 6 hours, use stored hot water
|  | How many hours per year is the heat needed? | 7008 | hrs/yr
| Distance | What is the distance between the heat sink and heat source? | 150 | ft
| Working Fluids | What are the working fluid(s) for the heat sink and source? | ammonia | n/a
| Current Heating System | What is the heating capacity of the facility’s current heating system? | 6 | MW
|  | What is the hot water temperature setpoint of the facility’s current heating system? | 145 | °F
What is the steam pressure setpoint of the facility’s current heating system?
|  | Are there other setpoints of the facility’s current heating system? Please specify in comments. |  | specify
|  | What is the baseload heat demand of the facility’s current heating system? | 1 | MW
|  | What is the peak heat demand of the facility’s current heating system? | 6 | MW
| Capacity Expansion | Do you want to expand your process heating capacity? If so, please explain in the comments. | no
|  | Do you want to expand your process cooling capacity? If so, please explain in the comments. | no
| Partial-Load Operation | How is partial-load operation planned (e.g., fixed volume flow, variable temperatures, etc.)? | Cycle off | n/a | Heats tank up to temp then shuts off
Energy-related requirements and costs
| Fuel Consumption and Costs | How much fuel did the process consume over the past 12 months? | 60 | MMBtu
|  | What fuel was used for the process? | natural gas | n/a
|  | What was your average fuel price over the past 12 months? | 6 | $/MMBtu
|  | Were these fuel prices fixed or variable? | variable | n/a
|  | Do you expect your fuel price to change in the next 12 months? If so, please explain in the comments. | yes | n/a | Varies significantly with spot market
|  | How much electricity did the process consume over the past 12 months? | 0 | kWh
|  | What was your average electricity price over the past 12 months? | 0.08 | $/kWh
|  | What was your average peak demand electricity price over the past 12 months? |  | $/kW
|  | Were these electricity prices fixed or variable? | variable | n/a
|  | Do you expect your electricity price to change in the next 12 months? If so, please explain in the comments. | yes | n/a | Modest increases
| Electrical Service | What is the total capacity (MW) of available electrical service on site? | 25 | MW
|  | How much electrical margin reserve do you have available on site? | 5 | MW
| Onsite Renewables | Are any renewable energy technologies (e.g., thermal energy storage tanks, electric boilers) already deployed on site? If so, please explain in the comments. | no | n/a
|  | Are you interested in integrating IHPs with other renewable energy technologies? | no | n/a | If appropriate
Environmental – Site considerations
| Site Temperatures | What is your site's average ambient air temperature (if seeking air source heat pump)?
What is your site's minimum ambient air temperature (if seeking air source heat pump)?
What is your site's maximum ambient air temperature (if seeking air source heat pump)?
| Noise Requirements | Do you have noise requirements to comply with? (E.g., according to OSHA, a worker should not be exposed to more than 85 dB of noise over an 8-hour period.) |  | n/a
| Floor Space | How much available floor space does your site have to accommodate a heat pump? | 1000 | ft2
| Refrigerants | Other than HVAC systems, what refrigerants do you have on site? | ammonia | n/a
|  | Do you have one or more preferred refrigerant? | ammonia | n/a
|  | Do you have any refrigerant restrictions? If so, please select from the dropdown and explain in the comments. |  | n/a
| Retrofits | Are you retrofitting an existing system or adding a new one? | retrofit | n/a
| Redundancy | Do you have redundancy requirements? If so, what are they? | no | n/a | Will use existing NG system as backup
Economic – Institutional and financial considerations
| Goals | What is your main goal in installing a heat pump (e.g., efficiency gains, cost savings, decarbonization targets)? | Cost savings, decarb targets | n/a
| Incentives | Have you accessed any utility, state, or federal incentives to help fund this heat pump project? If so, please select one or more funding types from the dropdown. | no | n/a
|  | Are you interested in any utility, state, or federal incentives to help fund this heat pump project? If so, please select one or more funding types from the dropdown. | interested in all (please elaborate in comments) | n/a
|  | Do you need to comply with any related requirements? Please explain in the comments. | no | n/a
| OpEx Requirements | Do you have internal operating expense (OpEx) or payback requirements? | Yes | n/a | 7 year max SPB for decarb projects
| Internal Carbon Price | If your company has set an internal carbon price, what is it? | 50 | $/MMT CO2
Regulatory – Certifications and compliance
| UL Certification | Do you need UL (Underwriters Laboratories) certification on the cabinet and/or the whole heat pump? | no | n/a
| Good Manufacturing Practices | Do you require GMP paperwork, or post-installation inspections? | yes | n/a
| Insurance | Do you need to comply with any requirements or standards from your insurance company? |  | n/a
| Local Codes | Do you need to comply with any local codes that might impact this project? | no | n/a

## 6. IHP Suppliers List
Instructions:
This list includes contact information for IHP manufacturers, vendors, and service providers. To send your completed toolkit Excel file to the full list of suppliers, copy the email addresses in column G and paste them into the bcc line of your email. You may also choose to email a subset of contacts in this list, directly email individual contacts, or share your completed toolkit with others.
Company | Website | Brief Description | Contact Type | Name | Title | Email | Phone Number
Airthium | https://airthium.com | We develop an ultra high temperature heat pumps. | Primary Point of Contact | Franck Lahaye | Cofounder | contact@airthium.com | (650) 200-7573
Armstrong International | https://armstronginternational.com/products-landing/heat-pump-packages/ | Armstrong International is a high temperature heat pump which can generate hot water or steam up to 120C/248F. | Primary Point of Contact | Rajkumar Gnanaraj | North America Technology Manager - Circular Thermal | rkumar@armstronginterntional.com | (269) 307-4531
AtmosZero, Inc. | https://atmoszero.energy/ | MW-scale drop-in electrified heat pumps for low-cost, decarbonized industrial steam | Primary Point of Contact | Ashwin Salvi | Chief Commerical Officer | ashwin@atmoszero.energy | (419) 351-1275
AtmosZero, Inc. | https://atmoszero.energy/ | MW-scale drop-in electrified heat pumps for low-cost, decarbonized industrial steam | Secondary Point of Contact | Nickolas Roberts | Senior Application Engineer | nickolas@atmoszero.energy
Echogen | echogen.com | Echogen is a world leader in developing closed-loop systems using carbon dioxide (CO2) as the working fluid, including heat engines (heat-to-power), heat pumps (power-to-heat) and Pumped Thermal Energy Storage (PTES) systems. Echogen's EPS100 is the largest, and to date only supercritical CO2 (sCO2) heat engine power cycle, licensed to Siemens for Oil and Gas applications and GE for marine applications. Echogen is leveraging their heat engine experience to develop innovative new high temperature CO2-based heat pumps for industrial decarbonization, including for process fluid heating for chemical and drying applications, and direct heat pump steam generation, including integration with thermal storage systems. | Primary Point of Contact | Timothy Held | CTO | theld@echogen.com | (234) 542-4379
Echogen | echogen.com | Echogen is a world leader in developing closed-loop systems using carbon dioxide (CO2) as the working fluid, including heat engines (heat-to-power), heat pumps (power-to-heat) and Pumped Thermal Energy Storage (PTES) systems. Echogen's EPS100 is the largest, and to date only supercritical CO2 (sCO2) heat engine power cycle, licensed to Siemens for Oil and Gas applications and GE for marine applications. Echogen is leveraging their heat engine experience to develop innovative new high temperature CO2-based heat pumps for industrial decarbonization, including for process fluid heating for chemical and drying applications, and direct heat pump steam generation, including integration with thermal storage systems. | Secondary Point of Contact | Philip Brennan | CEO | pbrennan@echogen.com | (234) 542-4379
Frick / Johnson Controls | https://www.johnsoncontrols.com/industrial-refrigeration | Johnson Controls Industrial Refrigeration is a leading developer and manufacturer of Refrigeration and Heating. Our modern cooling, heating, and energy solutions will provide you with the ability to reliably and precisely ensure the temperature of your industrial process. Johnson Controls Industrial Refrigeration offers products that are designed to work with your existing installation or packaged stand-alone products. | Primary Point of Contact | Curtis Rager | Product Manager - Heat Pumps | Curtis.G.Rager@jci.com | (717) 378-9187
Frick / Johnson Controls | https://www.johnsoncontrols.com/industrial-refrigeration | Johnson Controls Industrial Refrigeration is a leading developer and manufacturer of Refrigeration and Heating. Our modern cooling, heating, and energy solutions will provide you with the ability to reliably and precisely ensure the temperature of your industrial process. Johnson Controls Industrial Refrigeration offers products that are designed to work with your existing installation or packaged stand-alone products. | Secondary Point of Contact | Dave Eaton | Engineering Manager | David.E.Eaton@jci.com | (717) 762-2121
Frick / Johnson Controls | https://www.johnsoncontrols.com/industrial-refrigeration | Johnson Controls Industrial Refrigeration is a leading developer and manufacturer of Refrigeration and Heating. Our modern cooling, heating, and energy solutions will provide you with the ability to reliably and precisely ensure the temperature of your industrial process. Johnson Controls Industrial Refrigeration offers products that are designed to work with your existing installation or packaged stand-alone products. | Additional Contact | Oldrich Kolarik | Application Engineering Manager | Oldrich.Z.Kolarik@jci.com | (717) 762-2121
Frick / Johnson Controls | https://www.johnsoncontrols.com/industrial-refrigeration | Johnson Controls Industrial Refrigeration is a leading developer and manufacturer of Refrigeration and Heating. Our modern cooling, heating, and energy solutions will provide you with the ability to reliably and precisely ensure the temperature of your industrial process. Johnson Controls Industrial Refrigeration offers products that are designed to work with your existing installation or packaged stand-alone products. | Additional Contact | Bruce Straka | Application Engineer | Bruce.A.Straka@jci.com | (206) 226-7944
GEA | https://www.gea.com/en/products/heat-pumps/ | Solution provider either as component or equipment sales only or Turnkey Integrator (Sustainable Energy Solutions) of Industrial Heat Pumps and Industrial Chillers to either make hot water temperatures or Steam requirements for any type of Industry, process and market. | Primary Point of Contact | German Robledo | Industrial Heat Pump Sales Manager | german.robledo@gea.com | (717) 802-4843
GEA | https://www.gea.com/en/products/heat-pumps/ | Solution provider either as component or equipment sales only or Turnkey Integrator (Sustainable Energy Solutions) of Industrial Heat Pumps and Industrial Chillers to either make hot water temperatures or Steam requirements for any type of Industry, process and market. | Secondary Point of Contact | John Bowman | Director Applications Engineering | john.bowman@gea.com | (717) 472-8144
GEA | https://www.gea.com/en/products/heat-pumps/ | Solution provider either as component or equipment sales only or Turnkey Integrator (Sustainable Energy Solutions) of Industrial Heat Pumps and Industrial Chillers to either make hot water temperatures or Steam requirements for any type of Industry, process and market. | Additional Contact | Larry Bradley | Director New Equipment Sales | larry.bradley@gea.com | (717) 472-8199
GEA | https://www.gea.com/en/products/heat-pumps/ | Solution provider either as component or equipment sales only or Turnkey Integrator (Sustainable Energy Solutions) of Industrial Heat Pumps and Industrial Chillers to either make hot water temperatures or Steam requirements for any type of Industry, process and market. | Additional Contact | Simon Kelley | Heat Pump Product Manager | simon.keller@gea.com | (717) 879-5674
Karman Industries | karmanindustries.com | At Karman Industries we seek to revolutionize heat generation. We are developing a range of thermal energy products utilizing cutting-edge technology in turbomachinery, high-speed power electronics, and advanced manufacturing. We are beginning by developing mass manufactured, industrial heat pumps that cut operational costs for the largest global corporations and enable sustainable heat production. | Primary Point of Contact | David Tearse | Co-Founder and CEO | david@karmanindustries.com
Karman Industries | karmanindustries.com | At Karman Industries we seek to revolutionize heat generation. We are developing a range of thermal energy products utilizing cutting-edge technology in turbomachinery, high-speed power electronics, and advanced manufacturing. We are beginning by developing mass manufactured, industrial heat pumps that cut operational costs for the largest global corporations and enable sustainable heat production. | Secondary Point of Contact | CJ Kalra | Co-Founder and CTO | cj@karmanindustries.com
Nyle Thermal | https://nylethermal.com/ | Nyle Thermal is a subsidiary of Nyle Systems, a North American industry leader with 40 years of experience building industrial heat pumps. Our innovative solutions provide sustainable and efficient heating and cooling for a wide range of commercial and industrial applications with a focus on Thermal Energy Optimization within industrial plants. | Primary Point of Contact | Elmer Arbogast | Business Development Manager | earbogast@nyle.com | (800) 777-6953 Ext 700
Piller TSC Blower Corporation | www.piller.de | Piller is a global manufacturer of high-quality blowers and compressors that mechanically compress process vapors (MVC/MVR) to recover waste heat and supply it at a usable temperature. Operated as an Industrial Heat Pump, our blowers and compressors can achieve Coefficients of Performance (COP’s) between 5 to 45 and use steam or other existing process vapors at the plant as the refrigerant. With our innovative technology and expertise, we provide a critical component for creating sustainable steam-driven processes resulting in significant reductions in energy consumption and Scope 1 Emissions. | Primary Point of Contact | Caldwell Reed | VP of Sales & Project Management | caldwell.reed@piller.de | (518) 729-6048
Schneider Electric | perspectives.se.com | Schneider Electric is a leading Energy Services Company (ESCO) offering full turnkey design-build solutions for the deployment of industrial heat pumps and other types of thermal decarbonization measures at an individual site or enterprise level. We utilize in-house subject matter expertise and professional engineers, along with trusted design partners, to ensure every detail is accounted for from initial design to complete implementation. In addition, we offer performance guarantees of the systems and can arrange off-balance sheet, as-a-service model financing to fund these thermal decarbonization projects. | Primary Point of Contact | Kathleen Pratt | Program Manager | kathleen.pratt@se.com | (323) 203-6479
Schneider Electric | perspectives.se.com | Schneider Electric is a leading Energy Services Company (ESCO) offering full turnkey design-build solutions for the deployment of industrial heat pumps and other types of thermal decarbonization measures at an individual site or enterprise level. We utilize in-house subject matter expertise and professional engineers, along with trusted design partners, to ensure every detail is accounted for from initial design to complete implementation. In addition, we offer performance guarantees of the systems and can arrange off-balance sheet, as-a-service model financing to fund these thermal decarbonization projects. | Secondary Point of Contact | David Phillippe | Program Development Manager | david.phillippe@se.com | (615) 538-9781
Schneider Electric | perspectives.se.com | Schneider Electric is a leading Energy Services Company (ESCO) offering full turnkey design-build solutions for the deployment of industrial heat pumps and other types of thermal decarbonization measures at an individual site or enterprise level. We utilize in-house subject matter expertise and professional engineers, along with trusted design partners, to ensure every detail is accounted for from initial design to complete implementation. In addition, we offer performance guarantees of the systems and can arrange off-balance sheet, as-a-service model financing to fund these thermal decarbonization projects. | Additional Contact | David Kramer | Program Manager, North America | David.Kramer@se.com | (412) 680-5743
Siemens Energy, Inc. | https://www.siemens-energy.com/us/en/home/products-services/product-offerings/heat-pumps.html | Siemens Energy is a global leader in energy technology. For modern district heating and cooling or industrial heating applications, our large-scale industrial heat pumps (15-70 MWth) are the best and most efficient solution to convert electricity to heat. | Primary Point of Contact | Johnny Yan | Regional Sales Manager | johnny.yan@siemens-energy.com
Skyven Technologies | skyven.co | Skyven is an Energy-as-a-Service company pioneering the Skyven Arcturus line of industrial steam-generating heat pumps. Built using highly-reliable mechanical vapor recompression technology, Arcturus generates boiler-quality steam at 300 psig (420F) and temperature lifts up to 330F. Arcturus enables reductions in steam production costs by leveraging high COPs and fuel-switching benefits between electricity and natural gas. Additionally, Arcturus uses water as a 0 GWP refrigerant. | Primary Point of Contact | Jim Saccone | Senior VP of Global Sales | jim.saccone@skyven.co | (713) 248-0751
Spirax Sarco | www.spiraxsarco.com | Spirax Group focuses on providing sustainable solutions for steam and thermal applications. | Primary Point of Contact | Tye Buckley | Service Director | tye.buckley@us.spiraxsarco.com | (803) 603-9647
Thermal Energy International Inc. | www.thermalenergy.com | In short, Thermal Energy makes carbon reduction projects happen, and this includes application of a wide variety of heat pumps. TEI specializes in recovering and reusing waste heat (in the form of hot water), and then improving the quality of waste heat (to hotter water or steam) with heat pumps and mechanical vapor recompression. TEI provides services from portfolio energy and carbon analysis and modelling to determine most suitable carbon reduction technologies and projects for a customer, and then takes these projects and delivers them to our customers as turnkey projects with guaranteed outcomes. We deliver projects including our proprietary technologies and sometimes using off-the-shelf technologies, whatever provides our customer with the project that best meets their carbon reduction goals. | Primary Point of Contact | Robert Triebe | COO | robert.triebe@thermalenergy.com | (613) 371-6537
Thermal Energy International Inc. | www.thermalenergy.com | In short, Thermal Energy makes carbon reduction projects happen, and this includes application of a wide variety of heat pumps. TEI specializes in recovering and reusing waste heat (in the form of hot water), and then improving the quality of waste heat (to hotter water or steam) with heat pumps and mechanical vapor recompression. TEI provides services from portfolio energy and carbon analysis and modelling to determine most suitable carbon reduction technologies and projects for a customer, and then takes these projects and delivers them to our customers as turnkey projects with guaranteed outcomes. We deliver projects including our proprietary technologies and sometimes using off-the-shelf technologies, whatever provides our customer with the project that best meets their carbon reduction goals. | Secondary Point of Contact | David Coletta | Director of Strategic Partnerships | david.coletta@thermalenergy.com | (510) 284-2211
Trane Technologies | https://www.trane.com/commercial/north-america/us/en.html | Trane Technologies is a global climate innovator. Through our strategic brands Trane® and Thermo King®, and our portfolio of environmentally responsible products and services, we bring efficient and sustainable climate solutions to buildings, homes and transportation. We are now applying the vapor-compression cycle for Industrial Heat Pump applications. | Primary Point of Contact | Mike Filler | Regional Sustainable Systems Sales Leader | Mike.Filler@tranetechnologies.com | (719) 569-6977
Turboden S.p.A. | www.turboden.com | Turboden, a Mitsubishi Heavy Industries group company, is an Italian firm and a global leader during more than 40 years in the design, manufacture, and maintenance of Organic Rankine Cycle (ORC) systems. As part of MHI group Energy Transition Strategy, Turboden proposes high performance Large Heat Pumps capable to reach up to 250°C in a range of size starting from 5 to 40 MW heat production. Turboden's expertise lies in heat transfer, high temperatures, turbomachinery design, and natural refrigerant working fluids with the possibility of using HFOs if required. Such systems are highly customized and can be applied efficiently both in Industry (chemical, petrochemical, refinery, pulp & paper, food and beverage, carbon capture and storage, etc.) and in District Heating networks. | Primary Point of Contact | Emanuele Pingaro | Sales Manager Heat Generation Business Unit | emanuele.pingaro@turboden.it | +39 34 27626670
Turboden S.p.A. | www.turboden.com | Turboden, a Mitsubishi Heavy Industries group company, is an Italian firm and a global leader during more than 40 years in the design, manufacture, and maintenance of Organic Rankine Cycle (ORC) systems. As part of MHI group Energy Transition Strategy, Turboden proposes high performance Large Heat Pumps capable to reach up to 250°C in a range of size starting from 5 to 40 MW heat production. Turboden's expertise lies in heat transfer, high temperatures, turbomachinery design, and natural refrigerant working fluids with the possibility of using HFOs if required. Such systems are highly customized and can be applied efficiently both in Industry (chemical, petrochemical, refinery, pulp & paper, food and beverage, carbon capture and storage, etc.) and in District Heating networks. | Secondary Point of Contact | Davide Rizzi | Application Engineer | davide.rizzi@turboden.it | +39 34 29919535
Turboden S.p.A. | www.turboden.com | Turboden, a Mitsubishi Heavy Industries group company, is an Italian firm and a global leader during more than 40 years in the design, manufacture, and maintenance of Organic Rankine Cycle (ORC) systems. As part of MHI group Energy Transition Strategy, Turboden proposes high performance Large Heat Pumps capable to reach up to 250°C in a range of size starting from 5 to 40 MW heat production. Turboden's expertise lies in heat transfer, high temperatures, turbomachinery design, and natural refrigerant working fluids with the possibility of using HFOs if required. Such systems are highly customized and can be applied efficiently both in Industry (chemical, petrochemical, refinery, pulp & paper, food and beverage, carbon capture and storage, etc.) and in District Heating networks. | Additional Contact | Emanuele Mazzola | Sales Engineer | emanuele.mazzola@turboden.it | +39 34 72822032
Vilter by Copeland | https://www.copeland.com/en-us/products/refrigeration/industrial-refrigeration/industrial-heat-pumps | Vilter single screw industrial heat pumps deliver significant improvements in efficiency, reliability, and sustainability, challenging the status quo and accelerating the global energy transition. Leveraging our industry expertise, our natural refrigerant solutions help organizations and municipalities achieve their internal sustainability targets as part of their environmental, social, and governance (ESG) goals. | Primary Point of Contact | Gary Chafee | Director of Sales, Americas- Refrigeration & Heating | gary.chafee@copeland.com | (414) 403-7415
Vilter by Copeland | https://www.copeland.com/en-us/products/refrigeration/industrial-refrigeration/industrial-heat-pumps | Vilter single screw industrial heat pumps deliver significant improvements in efficiency, reliability, and sustainability, challenging the status quo and accelerating the global energy transition. Leveraging our industry expertise, our natural refrigerant solutions help organizations and municipalities achieve their internal sustainability targets as part of their environmental, social, and governance (ESG) goals. | Secondary Point of Contact | Grant Kovac | Director of Product Management | grant.kovac@copeland.com | (973) 407-9583
Suppliers may complete the form below to join this list:
Supplier Information Form
Suppliers can reach out to the ACEEE, NEMA, and RTC contacts on 1. Background & Instructions to make changes to the information listed above.

## Dropdown Options (hidden)
°F | MMBtu/hr | yes | water | steam | natural gas
°C | lb steam/hr | no | ammonia | water | coal
MMBtu/hr | kW | other (please specify in comments) | CO2 | glycol | liquid petroluem-based fuels
lb steam/hr | MW | multiple (please specify in comments) | hydrocarbons | ethanol | other oil products (please specify in comments)
m |  |  | propane | ammonia | non-fossil fuels: biomass (specify in comments)
ft |  | fixed | pentane | blend (please specify in the comments) | non-fossil fuels: other (specify in comments)
m2 |  | variable | HFCs | other (please specify in the comments) | n/a
ft2 |  | other (please specify in comments) | HFOs | multiple (please specify in the comments)
m3/hr |  |  | HCFOs
l/s |  | retrofit | HFC blend
bar |  | new | HFO blend
psi |  | other (please specify in comments) | HCFO blend
hrs/day |  |  | other blend (please specify in comments)
hrs/week |  | utility | other (please specify in comments)
hrs/year |  | state | multiple (please specify in the comments)
$/kWh |  | federal
$/MMBtu |  | no
$/therm |  | other (please specify in comments)
MMBtu |  | interested in all (please elaborate in comments)
therm
kW
MW
kWh